WROCLAW UNIVERSITY OF SCIENCE AND TECHNOLOGY

FACULTY OF ELECTRICAL ENGINEERING

Integr. of Distr. Res. in Pow. Lab                          Date 03/05/2022

Student name ………………………………….                        ID

Gebremeskel Dawit Gebreslassie……………...                    267607

Lab1 &2 -Load flow in radial network with DER

Table of Contents

1. Objective	2

2. Exercise description	2

3. Scheme of analyzed power system	2

4. Calculation of system parameters for a=61	3

5. Input data for a = 61	5

6. Load variations results	6

6.1 Load variation for 10 kv at the load bus	6

6.2 Load variation for 10.5Kv at load bus	8

6.3. Using the generator in bus 4 to increase transmission efficiency	10

7.Conclusion	12

# 1. Objective

The aim of this project is to acquire knowledge of the preparation of equivalent parameters of lines, cables and transformers which uses for load flow and voltage analysis for the given radial network in fig.1.

# 2. Exercise description

The given load variation for the given radial Network is 6 motors start (6S)

Induction motor voltage must not be less than 0.8UN and greater than 10.5 KV at the load bus. In each variation, the node load voltage should be changed to obtain the voltage 1.05UN, i.e., 10.5 kV at the feeder point.

# 3. Scheme of analyzed power system

# 4. Calculation of system parameters for a=61

Figure 2: Motor parameter calculation

Figure 3: Cable parameter calculation

Figure 4: Transformer parameter calculation

# 5. Input data for a = 61

function [nodes,branches,UN,U]=erlfd61

UN=10.0; % nominal voltage of equivalent network

U =10.0; % voltage set at the load bus

%

nodes=[

%   Pd(+)  - active load at node,

%   Pd(-)  - active injection at node

%   Qd(+)  - reactive load at node (inductive),

%   Qd(-)  - reactive injection at node (capacitive)

%   Un_kV  - nominal voltage of equivalent network

%   Uk_st  - voltage angle / zero before cload flow computing/

%Node   Un_kV    Uk_st      Pd_MW   Qd_Mvar

%   1       2    3           4      5

1   10.00    0          17.355    44.834

2   10.00    0          0          0

3   10.00    0          0          0

4   10.00    0          0          0

];

%

%

%

branches=[

%   k - node number at pi-end, p - node number at pi-begin

%   Sp=Pp+jQp--->p____R____X____k----> Sk=Pk+jQk

%   Up/Ukp       |              |      Uk/Ukk

%                Yp             Yk

%                |              |

%   -------------------------------------------

%

%   R - resistance, X - reactance

%   Yp=G/2+jB/2 - shunt admittance at pi-begin

%   Yk=G/2+jB/2 - shunt admittance at pi-end

% NOTE! B>0 for line and B<0 for transformer

% Give G,B w mikrosimens with proper sign:

%  (-)minus for transformer,

%  (+)plus for line

% Program creates pi-circuit with G/2 and B/2 so give G nad B.

%   p   k   R_om         X_om        G_mikroS       B_mikroS

%   1   2    3             4           5              6

2   1  0.071111     1.2125       49.161         -876.19

3   2  1.0534       0.6584           0          781.85

4   3  0.9984        0.624           0          741

];

%

return;

# 6. Load variations results

## 6.1 Load variation for 10 kv at the load bus

>> erlf

plikdat =

'erlfd61'

% Calculation stop:  2022- 5- 2  godz. 12h, 41min,  18.75s

Number of pi-circuits                npi =   3

Total bus number                       n =   4

Nominal voltage of equivalent network UN =   10.000 kV

Voltage set at load bus                U =   10.000 kV

czwornik   2 -   1

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

15.656  6.6  19.0043 0.0060   72.661  -0.1074   10.000  0.0  17.3550 0.0025   44.834  -0.0438

czwornik   3 -   2

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

20.399 -5.0  43.1850 0.0000   87.516  -0.1627   15.656  6.6  19.0043 0.0000   72.661  -0.0958

czwornik   4 -   3

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

25.358-11.7  65.9701 0.0000  101.364  -0.2382   20.399 -5.0  43.1850 0.0000   87.516  -0.1542

node   UN_kV     U_kV  dU_% Uk_st      P_MW      Q_MW

1   10.000   10.000   0.0   0.0   17.3550   44.8340

2   10.000   15.656  56.6   6.6   19.0043   72.6605

3   10.000   20.399 104.0  -5.0   43.1850   87.5155

4   10.000   25.358 153.6 -11.7   65.9701  101.3638

Active losses           Pstr =   48.615 MW

Transmission efficiency  eta =   26.307 %

End of calculation by erlf.m - see results in file erlfout.m>>

Figure 5:  Node voltage and current results for 10 KV

## 6.2 Load variation for 10.5Kv at load bus

>> erlf

plikdat =

'erlfd61'

% Calculation stop:  2022- 5- 7  godz. 13h, 41min,   5.06s

Number of pi-circuits                npi =   3

Total bus number                       n =   4

Nominal voltage of equivalent network UN =   10.000 kV

Voltage set at load bus                U =   10.500 kV

czwornik   2 -   1

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

15.881  6.1  18.8520 0.0062   70.048  -0.1105   10.500  0.0  17.3550 0.0027   44.834  -0.0483

czwornik   3 -   2

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

20.399 -4.8  40.7736 0.0000   83.488  -0.1627   15.881  6.1  18.8520 0.0000   70.048  -0.0986

czwornik   4 -   3

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

25.104-11.2  61.4238 0.0000   96.006  -0.2335   20.399 -4.8  40.7736 0.0000   83.488  -0.1542

node   UN_kV     U_kV  dU_% Uk_st      P_MW      Q_MW

1   10.000   10.500   0.0   0.0   17.3550   44.8340

2   10.000   15.881  58.8   6.1   18.8520   70.0475

3   10.000   20.399 104.0  -4.8   40.7736   83.4878

4   10.000   25.104 151.0 -11.2   61.4238   96.0065

Active losses           Pstr =   44.069 MW

Transmission efficiency  eta =   28.255 %

End of calculation by erlf.m - see results in file erlfout.m>>

Figure 6:  Node voltage and current results at 10.5 Kv

## 6.3. Using the generator in bus 4 to increase transmission efficiency

In this case unlike the above two cases the generator in bus 4 will operate at power factor 1 (cosfi=1). The input data in this case will look like as shown below

%Node   Un_kV    Uk_st      Pd_MW   Qd_Mvar

%   1       2    3           4         5

1   10.00    0        17.355   44.834

2   10.00    0          0          0

3   10.00    0          0          0

4   10.00    0         14.1        0

Because of this the transmission efficiency increase to a great extent comparing with the other two cases. The result is shown below.

>> erlf

plikdat =

'erlfd61'

% Calculation stop:  2022- 5- 4  godz.  9h, 31min,  22.93s

Number of pi-circuits                npi =   3

Total bus number                       n =   4

Nominal voltage of equivalent network UN =   10.000 kV

Voltage set at load bus                U =   10.500 kV

czwornik   2 -   1

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

15.881  6.1  18.8520 0.0062   70.048  -0.1105   10.500  0.0  17.3550 0.0027   44.834  -0.0483

czwornik   3 -   2

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

20.399 -4.8  40.7736 0.0000   83.488  -0.1627   15.881  6.1  18.8520 0.0000   70.048  -0.0986

czwornik   4 -   3

Up_kV Ukp_st  Pp_MW dPp_MW  Qp_Mvar dQp_Mvar    Uk_kV Ukk_st  Pk_MW dPk_MW  Qk_Mvar dQk_Mvar

25.104-11.2  61.4238 0.0000   96.006  -0.2335   20.399 -4.8  40.7736 0.0000   83.488  -0.1542

node   UN_kV     U_kV  dU_% Uk_st      P_MW      Q_MW

1   10.000   10.500   0.0   0.0   17.3550   44.8340

2   10.000   15.881  58.8   6.1   18.8520   70.0475

3   10.000   20.399 104.0  -4.8   40.7736   83.4878

4   10.000   25.104 151.0 -11.2   75.5238   96.0065

Active losses           Pstr =   44.069 MW

Transmission efficiency  eta =   41.649 %

End of calculation by erlf.m - see results in file erlfout.m>>

Figure 7:  Node voltage and current results when Generator in bus 4 operates

# 7.Conclusion

Three different cases are selected to perform this task at the given load as listed below.

- The first case is performed at 10Kv at the load bus. At this voltage level, the active power losses is 48.615 MW, transmission efficiency is 26.307 %, and supply voltage is 25.358Kv

- The second case is performed for 10.5Kv load bus. At this voltage level, the active power losses is 44.069 MW and transmission efficiency is 28.255 %, and supply voltage is 25.104Kv

- The third case is performed at 10.5Kv with the generator in bus 4 operating to increase the transmission efficiency. While the active power losses is still the same (44.069 MW) because the generator is operating at power factor 1, but the transmission efficiency is this time 41.649 %. Which is big improvement compared with the above two cases in which the generator was not operating.

Although the goal is to reach 10.5 Kv at the feeder point, this is not possible due to the very high reactive power requirements of the motors. All 6 motors are starting in this case, which requires 17.355 Mw real and 44.834 Mvar reactive power. This very high reactive power requirement shows that a very high voltage is required to increase transmission efficiency and reduce active losses. However, we cannot arbitrarily increase the voltage in the load bus, since this requires a high supply voltage, which is above the rated voltage.

In summary, as the voltage in the load bus increases the transmission efficiency increases and the active power loss decreases. Moreover, the transmission efficiency increases when the generator in bus 4 operates at good power factor as it is demonstrated in case 3.